## AS4041 Straight Internal
AS4041 PRESSURE PIPING - ALLOWABLE DESIGN PRESSURE
Weld Joint Factor (AS4041 Table 3.12.2 or D12) | e | 1 | Product of e x M not less than 0.7
Class Design Factor (AS4041 Table 3.12.3) | M | 1 | e x M | 1
Design Temperature, °C | T | 525
Weld Joint Strength Reduction Factor (AS4041 Table 3.12.5) | W | 0.97541
Material Design Strength, MPa (AS4041, Appendix D) | f | 82.68
Pipe Outside Diameter from Pipe Charts, mm | D | 273.2
Nominal Wall Thickness from Pipe Charts, mm | tm | 12.77 | Manufacturing Tolerances
Manufacturing Tolerance (± %) |  | 12.5 | Aust Pipes ± 10%; American Pipes ± 12.5%
Corrosion Allowance, mm | G | 1.6
Depth of Threading, Grooving or Machining, mm |  | 0
Pressure Design Wall Thickness, mm | tf | 9.5738
Maximum Allowable Design Pressure, MPa | MADP | 5.8575
AS4041 PRESSURE PIPING - REQUIRED PRESSURE DESIGN WALL THICKNESS
Weld Joint Factor (AS4041 Table 3.12.2 or D12) | e | 1 | Product of e x M not less than 0.7
Class Design Factor (AS4041 Table 3.12.3) | M | 1 | e x M | 1
Design Temperature, °C | T | 525
Weld Joint Strength Reduction Factor (AS4041 Table 3.12.5) | W | 0.97541
Material Design Strength, MPa (AS4041, Appendix D) | f | 82.68
Pipe Outside Diameter from Pipe Charts, mm | D | 273.2
Manufacturing Tolerance (± %) |  | 12.5 | Manufacturing Tolerances
Corrosion Allowance, mm | G | 1.6 | Aust Pipes ± 10%; American Pipes ± 12.5%
Depth of Threading, Grooving or Machining, mm |  | 0
Design Pressure, MPa | p | 5.82
Pressure Design Wall Thickness, mm | tf | 9.5146
Required Wall Thickness (including allowances), mm | tm | 12.7024 | Therefore Choose DN250 S/S pipe will a nominal thickness > 12.7 mm

## ASME B31.3 Straight Internal
ASME B31.3 PROCESS PIPING - ALLOWABLE DESIGN PRESSURE
Weld Joint Quality Factor (ASME B31.3 Table 302.3.4) | Ej | 1 | Seamless ASTM A312 TP304
Coefficient Y (ASME B31.3 Table 304.1.1) | Y | 0.4
Design Temperature, °C | T | 525 | 975°F
Weld Joint Strength Reduction Factor (ASME B31.3 Cl. 302.3.5(e)) | W | 0.97541
Material Allowable Stress, MPa (ASME B31.3 Table A-1M) | S | 97.3 | 12 ksi
Pipe Outside Diameter from Pipe Charts, mm | D | 273.1575 | 10.75"
Nominal Wall Thickness from Pipe Charts, mm | tm | 12.77 |  | Manufacturing Tolerances
Manufacturing Tolerance (± %) |  | 12.5 |  | Aust Pipes ± 10%; American Pipes ± 12.5%
Corrosion Allowance, mm | c | 1.5881
Depth of Threading, Grooving or Machining, mm |  | 0
Pressure Design Thickness, mm | t | 9.5856
Maximum Allowable Internal Design Gauge Pressure, MPa | MADP | 6.8534
ASME B31.3 PROCESS PIPING - REQUIRED PRESSURE DESIGN WALL THICKNESS
Weld Joint Quality Factor (ASME B31.3 Table 302.3.4) | Ej | 1 | Seamless ASTM A312 TP304
Coefficient Y (ASME B31.3 Table 304.1.1) | Y | 0.4
Design Temperature, °C | T | 525 | 975°F
Weld Joint Strength Reduction Factor (ASME B31.3 Cl. 302.3.5(e)) | W | 0.97541
Material Allowable Stress, MPa (ASME B31.3 Table A-1M) | S | 97.3 | 12 ksi
Pipe Outside Diameter from Pipe Charts, mm | D | 273.1575 | 10.75"
Manufacturing Tolerance (± %) |  | 12.5 |  | Manufacturing Tolerances
Corrosion Allowance, mm | G | 1.5881 |  | Aust Pipes ± 10%; American Pipes ± 12.5%
Depth of Threading, Grooving or Machining, mm |  | 0
Design Pressure, MPa | P | 5.822 | 845 psi
Pressure Design Thickness, mm | t | 8.1777 | 0.32183 | inches
Minimum Required Thickness (including allowances), mm | tm | 11.1609 |  | 0.43923 | inches
Therefore Choose DN250 S/S pipe will a nominal thickness > 12.77 mm

## AS4041 Bend Internal
AS4041 PRESSURE PIPING - REQUIRED PRESSURE DESIGN WALL THICKNESS FOR BENDS
Weld Joint Factor (AS4041 Table 3.12.2 or D12) | e | 1 | Product of e x M not less than 0.7
Class Design Factor (AS4041 Table 3.12.3) | M | 1 | e x M | 1
Design Temperature, °C | T | 525
Weld Joint Strength Reduction Factor (AS4041 Table 3.12.5) | W | 0.97541
Bend Radius, measured to pipe centreline, mm | R1 | 1270
Material Design Strength, MPa (AS4041, Appendix D) | f | 82.68
Pipe Outside Diameter from Pipe Charts, mm | D | 273.2
Manufacturing Tolerance (± %) |  | 12.5 | Manufacturing Tolerances
Corrosion Allowance, mm | G | 1.6 | Aust Pipes ± 10%; American Pipes ± 12.5%
Depth of Threading, Grooving or Machining, mm |  | 0
Design Pressure, MPa | p | 5.82
"I" at the Intrados | I | 1.0603
"I" at the Extrados | I | 0.95144
Pressure Design Wall Thickness @ Intrados, mm | tf | 8.9916 | Problem with AS4041 formula compared to ASME B31.3 formula.
Pressure Design Wall Thickness @ Extrados, mm | tf | 9.9825 | The intrados should get thicker and the extrados thinner.
Required Wall Thickness @ Intrados, mm | tm | 12.1047 | As thickness is "lost"during the bending process, it would be normal
Required Wall Thickness @ Extrados, mm | tm | 13.2371 | to multiply the required wall thickness at the extrados by a factor of
1.1 to 1.125 dependent upon how "tight"the bend radius is. The resulting
value will give the nominal thickness of pipe required for bending.

## ASME B31.3 Bend Internal
ASME B31.3 PROCESS PIPING - REQUIRED PRESSURE DESIGN WALL THICKNESS FOR BENDS
Weld Joint Quality Factor (ASME B31.3 Table 302.3.4) | Ej | 1
Coefficient Y (ASME B31.3 Table 304.1.1) | Y | 0.4
Design Temperature, °C | T | 525
Weld Joint Strength Reduction Factor (ASME B31.3 Cl. 302.3.5(e)) | W | 0.97541
Bend Radius, measured to pipe centreline, mm | R1 | 1270
Material Allowable Stress, MPa (ASME B31.3 Table A-1M) | S | 82.68
Pipe Outside Diameter from Pipe Charts, mm | D | 273.2
Manufacturing Tolerance (± %) |  | 12.5 | Manufacturing Tolerances
Corrosion Allowance, mm | G | 1.6 | Aust Pipes ± 10%; American Pipes ± 12.5%
Depth of Threading, Grooving or Machining, mm |  | 0
Internal Gauge Pressure, MPa | P | 5.82
"I" at the Intrados | I | 1.0603
"I" at the Extrados | I | 0.95144
Pressure Design Thickness @ Intrados, mm | t | 10.1416
Pressure Design Thickness @ Extrados, mm | t | 9.1286
Required Wall Thickness @ Intrados, mm | tm | 13.419 | As thickness is "lost"during the bending process, it would be normal
Required Wall Thickness @ Extrados, mm | tm | 12.2612 | to multiply the required wall thickness at the extrados by a factor of
1.1 to 1.125 dependent upon how "tight"the bend radius is. The resulting
value will give the nominal thickness of pipe required for bending.